## (a)Node
Table 2.4 (a) Sample Node data
| Node type | PV/PQ | Load | Load | [5 empty] | Voltage(kV)
Node | N - Bus |  | type | priority | P | Q | Capacity | Initial | Annual
| V - Virtual bus | 0- None | G-Gen. |  | Load | Load |  | phase | Failure
Number | J - Junction | 1- PQ | I-Industrial | 1-High |  |  |  | angle | rate | Rated | Lower | Upper
| C - Line type change point | 2- PV | C-Commercial | 2-Middle | (MW) | (Mvar) | (MVA) |  | (time/year)
| H - Parallel lines change point | S-Slack | R-Residential | 3-Low
221 | N | 1 | [6 empty] | 0.0001 | 66 | 60 | 72
222 | N | 1 | [6 empty] | 0.0001 | 66 | 60 | 72
2o11 | V | 0 | [7 empty] | 66 | 60 | 72
2o12 | V | 0 | [7 empty] | 66 | 60 | 72
14o11 | V | 0 | [7 empty] | 66 | 60 | 72
14o12 | V | 0 | [7 empty] | 66 | 60 | 72
1401 | N | 1 | [6 empty] | 0.0001 | 66 | 60 | 72
1402 | N | 1 | [6 empty] | 0.0001 | 66 | 60 | 72
1481 | N | 0 | [6 empty] | 0.0001 | 66 | 60 | 72
1491 | N | 0 | R | 3 | 7.8 | 1.6 | 10 |  | 0.0001 | 6.6 | 6 | 7.2
14D1 | V | 0 | [7 empty] | 6.6 | 6 | 7.2
14DT | V | 0 | [7 empty] | 6.6 | 0 | 7.2
312o1 | V | 0 | [7 empty] | 66 | 60 | 72
312o2 | V | 0 | [7 empty] | 66 | 60 | 72
31200 | N | 1 | C | 2 | 2.1 | 0.4 |  |  | 0.0001 | 66 | 60 | 72
51011 | J | 0 | [7 empty] | 66 | 60 | 72
51012 | J | 0 | [7 empty] | 66 | 60 | 72
Note ;
There are 3 Node numbering schemes, depending on node type.
a. Substations and customer bus node (3-5 digits)
| Substation No.(1-3digits) + Bus No.(2digits) | [8 empty] | Example：1402
b. Virtual nodes in substations and switching stations.
| Substation No.(1-2digits) + Bus No.(1 letter + 1-2digits) | [8 empty] | Example：2o21
c. Nodes on transmission lines.
| Route No.(1-2digits) + Serial No.(2digits) + Circuit No.(1digit) | [8 empty] | Example：51012
Example of Node/Switchgear numbers
| Substation 2 |  |  | Customer 312 |  |  |  |  | Switching station 14
| ↑ 221 |  |  | 31200 |  |  |  |  | 14o10
[7 empty] | 1402 |  |  |  | 1401
312o1
| ↓ 222 | [9 empty] | 14o81
|  |  | 2o20 | [5 empty] | 14o11
[6 empty] | 312o1 |  |  | 14o11 |  | 14o82
| 2o22 |  | 312o2 |  |  | 14o12
| 2o22 |  | 312o2 |  |  | 51011
1481
|  | 2o21 | 2o21 |  |  | ルート51 |  | 14D1
14L301
| - Circuit Breaker |  |  |  | 51012 |  |  | 14L350
| - Line switch | [5 empty] | 14o12 |  | 14DT
| - On-load switch |  |  | Italic - Swithgears | [5 empty] | 1491
Node type : |  | N - Bus node |  |  | : Denotes normal bus
|  | J - Junction node |  |  | : Denotes transmission line junctions
|  | C - Line type change point |  |  | : Denotes transmission line change point
|  | H - Parallel Line change point |  |  | : Denotes transmission parallel line state change point
|  | V - Virtual node |  |  | : Denotes virtual nodes connecting switchgears with branches.
PV/PQ : |  | : Denotes fixed parameters when conducting power flow simulations.

## (b)Transmission line
Table 2.4 (b) Sample transmission lines data
Line | Data type | From | To | Line type | Length | Continuous |  | Short-time |  | Parallel | %Impedance
| T -O/H lines |  |  |  |  | Capacity |  | Capacity |  | Branch | (10MVA base)
Number | U -Cables | Node | Node |  | (km) | (MW) | (A) | (MW) | (A) |  | Z1R | Z1X | Y1C
51011 | T | 2o21 | 51011 | ACSR410 | 6.8 | 90 | 830 | 102 | 937 | 51012 | 0.1101 | 0.5623 | 0.48
51012 | T | 2o22 | 51012 | ACSR410 | 6.8 | 90 | 830 | 102 | 937 | 51011 | 0.1101 | 0.5623 | 0.48
51021 | T | 51011 | 14o11 | ACSR410 | 2.16 | 90 | 830 | 102 | 937 | 51022 | 0.035 | 0.1786 | 0.15
51022 | T | 51012 | 14o12 | ACSR410 | 2.16 | 90 | 830 | 102 | 937 | 51021 | 0.035 | 0.1786 | 0.15
51051 | U | 51011 | 312o1 | 3*CV400 | 1.57 | 61 | 560 | 61 | 560 |  | 0.0169 | 0.0427 | 2.9
51052 | U | 51012 | 312o2 | 3*CV400 | 1.57 | 61 | 560 | 61 | 560 |  | 0.0169 | 0.0427 | 2.9
Notes ;
| Transmission line No.(5digits) |  | Route No.(2digits) + Section No.(2digits) + Circuit No.(1digit)
|  | Example：51011→ |  | 5 1 | 0 1 |  |  |  | 1
|  |  |  | route 51 | first section |  |  |  | No.1 circuit
The above line data corresponds to the system diagram shown on Table 2.4.
Parallel branch No. is supplied to simulate transmission route faults during reliability assessment simulations.

## (c)Switchgear
Table 2.4 (c) Sample Switchgears data
Switchgear | Data type | From | To Node 1 |  | To Node 2 |  | Failure | Number of switchgears
Number | B - Circuit Breaker | Node | Number | On/Off | Number | On/Off | rate | CB | LS | OLS
| S - Line switch | Number |  | 0-Off |  | 0-Off | (time/year)
| L - On-load switch |  |  | 1-On |  | 1-On
2o20 | B | 221 | 222 | 1 |  |  | 0.00048 | 1 | 2 | 0
2o21 | B | 2o21 | 221 | 1 | 222 | 0 | 0.00061 | 1 | 3 | 0
2o22 | B | 2o22 | 221 | 0 | 222 | 1 | 0.00061 | 1 | 3 | 0
14o10 | B | 1401 | 1402 | 1 |  |  | 0.00048 | 1 | 2 | 0
14o11 | B | 14o11 | 1401 | 1 |  |  | 0.00048 | 1 | 2 | 0
14o12 | B | 14o12 | 1402 | 1 |  |  | 0.00048 | 1 | 2 | 0
14o81 | B | 1402 | 1481 | 1 |  |  | 0.00048 | 1 | 2 | 0
14o82 | B | 1402 | 1483 | 0 |  |  | 0.00048 | 1 | 2 | 0
18L301 | L | 14D1 | 1491 | 1 |  |  | 0.00011 | 0 | 0 | 1
18L350 | L | 1491 | 14DT | 0 |  |  | 0.00011 | 0 | 0 | 1
312o1 | B | 312o1 | 31200 | 1 |  |  | 0.00048 | 1 | 2 | 0
312o2 | B | 312o2 | 31200 | 0 |  |  | 0.00048 | 1 | 2 | 0
Note ;
Switchgears numbering (Max 7 digits)
Substation/Customer No. (1-3digits) + Switchgears No. (1 letter + 1-3 digits)
Designation of From/To nodes.
/If there are no branching, the node that does not belong to a bus becomes the 'From' node.
If both sides are bus nodes, the younger node becomes the 'From' node.
/If the switchgear branches out (e.g.. As switchgear 2o21), then the fixed end becomes the 'From' node:
I.e. In the case of a switchgear connected to double-bus substation, the line-side node becomes the 'From' node.
In a case of a single switchgear feeding 2 lines, the bus side node becomes the 'From' node.

## (d)Transformer bank
Table 2.4 (d) Sample transformer banks data
Trans. | Data type | Node number |  | Capacity | Rated Voltage(kV) |  | Node with fixed tap | Tap voltage(kV) |  |  | Failure rate | % X
Number | X - Trans. | From | To | (MVA) | From | To | 0Both,1Primary,2Secondary | Upper | Lower | Number | (time/year) | (10MVA)
110 | X | 1o11 | 1o21 | 200 | 275 | 66 | 2 | 302 | 248 | 23 | 0.00167 | 1.02
120 | X | 1o12 | 1o22 | 200 | 275 | 66 | 2 | 302 | 248 | 23 | 0.00167 | 0.976
211 | X | 2o11 | 271 | 200 | 154 | 66 | 2 | 161 | 133 | 17 | 0.00167 | 0.88833
212 | X | 271 | 2o21 | 200 | 66 | 66 | 0 |  |  |  | 0.00167 | -0.07833
213 | X | 271 | 291 | 200 | 66 | 22 | 0 |  |  |  | 0.00167 | 1.2117
1530 | X | 1581 | 1591 | 10 | 66 | 6.6 | 1 | 6 | 7.2 | 17 | 0.00167 | 7.5
1540 | X | 1582 | 1592 | 15 | 66 | 6.6 | 1 | 6 | 7.2 | 17 | 0.00167 | 5
1550 | X | 1583 | 1593 | 20 | 66 | 6.6 | 1 | 6 | 7.2 | 17 | 0.00167 | 3.75
Notes ;
Transformer bank numbering (3-5digits)
Substation No.(1-3digits) + Serial No.(1digit) + Primary/Secondary/Tertiary(1digit)
| Example 212: |  |  | 2 |  | 1 |  | 2
|  |  |  | No.2 substation |  | No.1 Trans. |  | Secondary
If there are no tertiary, put '0' for the final digit.

## (e)Voltage compensator
Table 2.4 (e) Sample voltage compensators data
Number | Data type | Connected | Capacity |  | Rated | On/Off
| C - Cs | Bus | (MVA) |  | Voltage | 0 - Off
| R - ShR |  | C | L | (kV) | 1 - On
2C11 | C | 291 | 15 |  | 22 | 0
2C12 | C | 291 | 15 |  | 22 | 1
2C13 | C | 291 | 20 |  | 22 | 0
18C1 | C | 1811 | 15 |  | 66 | 0
18C2 | C | 1812 | 15 |  | 66 | 1
124C1 | C | 12421 | 4 |  | 6.6 | 0
Note :
Voltage compensator numbering
Substation No.(1-3digits) + Data type(1 letter) + Serial No.(1-3digits)